## vir-850 specification
VIR-850 series Flanged In-Line Type Flow/Heat meter with Integrated transmitter or VIR-832-M remote Transmitte
Main Unit | Accuracy | Class 2 -EN 1434 Standard
| Repeatability | Better than 1%
| Principle | Transit-time measuring principle
| Measurement Period | 500ms
| Display | LCD with backlight, display accumulated flow/heat, instantaneous flow/heat, velocity, time etc.
| Output | Analog output: 4-20mA or 0-20mA current output. Impedance 0.1kw. Accuracy 0.1%
OCT output: Frequency signal (1-9999HZ)
Relay output: Programmable (no signal, reverse flow etc.)
RS-485 serial port
| Input | 1 analog input
| RTD For Heat Meter only | Two 2-wire, 3-wire Pt100/Pt1000/Pt 500 RTD 12-bit inputs; Range of –40° C…200° C; Clamp-on resistor kits available
| Other functions | Automatically record the totaliser data upto 5 years and 16 years option
| Energy total (Heat Meters) | British Thermal Unit (Btu), MWH KWH
| Heat/cooling rate (Heat Meters) | Btu/hour, Kilowatts, Megawatts,
| Temperature (Heat Meters) | Fahrenheit, Celsius
| Power loss mode | The power-on time and corresponding flow rate of the last 64 power on and off events. Allow manual or automatic flow loss compensation
Pipe | Material | Steel, Stainless steel, Cast iron, Cement pipe, Copper, PVC, Aluminium, FRP etc. Liner is allowed
| Size | 50-800mm
| Straight pipe section | In the upstream it must be beyond 10D, in the downstream it must be beyond 5D. In the upstream the length must be beyond 30D from the access of the pump. (D Stands for pipe diameter)
Liquid | Types | Water, sea water, industrial sewage, acid and alkali liquid, alcohol, beer, all kinds of oils which can transmit ultrasonic single uniform liquid
| Temperature | Standard : -10° C - 160° C
| Turbidity | Less than 10000ppm, with a little bubble
| Flow Direction | Bi-directional measuring, net flow/heat measuring
Environment | Ambient Temperature | Main Unit: -–4…140° F (–20…60° C)
| Altitude Restriction | Up to 2000 m (6561 ft)
| Humidity | Main Units:0…85%, non-condensing
Transducer : water-immersible, water depth less than 3m
Cable | Twisted pair line, standard length of 20m, can be extended to 500m (not recommended); Contact the manufacturer for longer cable requirement. RS-485 interface, transmission distance up to 1000m
Power Supply | DC24V
Power | Less than 1.5W
Protocols | MODBUS-RTU Protocol Standard. Option of BACnet MS/TP or IP with MC-603 Kamstrup make calculator available.

## dimension
Model | Nominal Diameter (DN) | Flow Nominal M3/Hr | P/N P | Width W | Height H | Outer Diameter D | Bolt Hole Centers D1 | Bolt Hole X Quantity ∮X n | Sealing Surface Diameter D2 | Flange Thickness |  | Bolt Specification
[10 empty] | c | f
65-UF-VIR-850 | 125 | 100 | 1.6 | 250 | 428 | 250 | 210 | 18x 8 | 184 | 22 | 2 | M2 0x 80
65-UF-A-VIR-850 | 150 | 150 | 1.6 | 285 | 459 | 285 | 240 | 22x 12 | 211 | 24 | 2 | M2 0x 90
65-UF-B-VIR-850 | 200 | 250 | 1.6 | 340 | 511 | 340 | 295 | 26x 12 | 266 | 26 | 2 | M2 2x 90
65-UF-C-VIR-850 | 250 | 400 | 1.6 | 405 | 569 | 405 | 355 | 26x 12 | 319 | 28 | 2 | M2 2x 90
65-UF-D-VIR-850 | 300 | 600 | 1.6 | 460 | 621 | 460 | 410 | 23x 16 | 370 | 32 | 2 | M2 2x 90
65-UF-E-VIR-850 | 350 | 800 | 1.6 | 500 | 666 | 500 | 460 | 25x 16 | 428 | 28 | 4 | M2 0x 80
65-UF-F-VIR-850 | 400 | 1000 | 1.6 | 565 | 697 | 565 | 515 | 25x 20 | 482 | 30 | 4 | M2 2x 90
65-UF-G-VIR-850 | 450 | 1200 | 1 | 615 | 774 | 615 | 565 | 25x 20 | 532 | 30 | 4 | M2 2x 90
65-UF-H-VIR-850 | 500 | 3000 | 1 | 670 | 826 | 670 | 620 | 30x 20 | 585 | 32 | 4 | M2 2x 90
65-UF-I-VIR-850 | 600 | 4400 | 1 | 780 | 931 | 780 | 725 | 25x 24 | 685 | 36 | 5 | M 27x 110
65-UF-J-VIR-850 | 700 | 6200 | 0.6 | 860 | 1021 | 860 | 810 | 30x 24 | 775 | 32 | 5 | M2 2x 90
65-UF-K-VIR-850 | 800 | 8000 | 0.6 | 975 | 1129 | 975 | 920 | 30x 24 | 880 | 32 | 5 | M 27 x 100
*All Dimensions in mm. +/- 3% variation.